| Description: | Tank and Pump Skid |
| --- | --- |
| Quantity: | 1 |
| Usage: |  |
| Condition: | New |
| Location: | NE BC |

| Specifications: | Tanks:  (2) 2200 L Double walled tank, 50 ID x 72 Long, 7 Kpa max op. pressure (Clemmer)  (2) 3050 L Double walled tank, 50 ID x 98.5 Long, 7 Kpa max op. pressure (Clemmer)  ASTM A36 / 36M construction, ULC S601 double wall standard  Each tank includes two sight level gauges with isolation valves  Support stand built with structural HSS tubing and wide flange beam  (CWB Certified welding) Building:  12-0 wide x 25-0 long x 13-0 low eave, 14-0 high eave, shed style roof with a 1:12 slope  22 gauge pre-painted exterior walls, roof and trim (Warwick standard stock colors)  R-12 fibre glass batt insulation in the walls and R-20 in roof with a 6-mil vapor barrier throughout  24 gauge white fluted aluminum interior liner  (2) 6 x 7 double steel man door (16 ga frame, 18 ga door, R12 insulated) c/w 88TP locking panic hardware, hydraulic door closure, IWG window in both leafs, kick plates, aluminum threshold, check chain, weather-stripping and canopy  (3) 12 x 12 stamped louvers c/w interior sliders and (1) 36 x 36 Sliding Window  (1) 12 explosion proof exhaust fan c/w hood, 120/1/60 (based on 12 ACPH)  (1) Ruffneck FX5 electric heater |
| --- | --- |

Skid

 12 x 25 skid, 12 wide flange construction, checker plate floor, lifting lugs, and high density foam insulation applied to bottom of skid (CWB Certified welding)

 P. Eng stamped design (BC Registered)

Paint

 Sandblast to SSPC SP-6 Spec

 1 Coat of Tan Cloverdale DTM Paint

Pump System & Piping:

 1 SS Autoclave tubing, valves, and fittings will be supplied by others for P-111 pump discharge

 1/2 316SS Swagelok tube fittings with twin ferrule valves will be used for P-113 pump discharge

 Techlok fittings will be supplied by Ultrafab

 Flexible hose will be used on the pump suction lines, 316SS inner bellows with 304SS outer braid

 (3) 1 x 1 NPT 316SS Farris PSVs for pump recycle bypass

 (3) Pressure Switches - 1/2" NPT, Electric, 3000psi MAWP (CCS

 6900GZE22)

Electrical

 Building Area Classification - Class 1, Div 2 as per Canadian Electrical Code

 Low voltage installation will be done using aluminum conduit and (1)

 Hammond junction box Brands used are Crouse-Hinds, Hoffman, Meyers, and Weidmuller

 a. (4) Crouse-Hind On/Off switches, one for each pump and one for the heater.

 b. (1) Det-Tronics MIR flame detector with Carbon Controls beacon.

 c. (1) Carbon Controls ESD mushroom push button w/ safety shroud

 d. (1) Exhaust fan - 12 x 12, explosion proof

